## Boiler
Template Category | Boiler with Integrated Burner - Gas or Oil
Template Version | v3
Category Description | Gas & Oil Fired Boiler used for space heating and indirect hot water generation with integrated burner
Classification System
Classification | Value
Suitability for Use | Approved
Template Custodian | CIBSE
Information Category | Parameter Name | Value | Units | Notes
Manufacturer Data
Specifications | Manufacturer | Bosch Thermotechnology | Text
Specifications | Manufacturer Website | www.bosch-industrial.co.uk | URL
Specifications | Product Range | GE615 | Text
Specifications | Product Model Number | 570kW | Text | Or Code
Specifications | CE Approval | CE-0461 AU 417 | Text | Number, Yes, No
Specifications | Product Literature | http://www.bosch-industrial.co.uk/GE615 | URL
Specifications | Additional Technical Details | http://www.bosch-industrial.co.uk/GE615 | URL | URL to technical details, e.g. system flow rates, pressure drop curves
Specifications | Features | High Efficiency Cast Iron Boiler | Text | Free text to describe product
Construction Data
Specifications | Type | Space heating | Text
Specifications | Configuration | Single boiler | Enumeration
Specifications | Shape | Rectangular (Horizontal) | Enumeration
Specifications | External Material | Steel | Enumeration
Specifications | Colour | Blue RAL Classic 5005 | Text | e.g. RAL, Colour
Specifications | Finish | Paint | Text | e.g. Anodised, Brushed, Painted, Natural (Self-finish)
Specifications | Mounting | Floor Standing | Enumeration
Specifications | Burner Control Type | Unset | Enumeration
Specifications | Heater Operation | Non condensing | Enumeration | State whether product has condensing function
Specifications | Heat Exchanger Material | Cast Iron | Enumeration
Specifications | Fuel Connection Type | Unset | Enumeration
Specifications | Flow and Return Connection Type | Flanged | Enumeration
Specifications | Drain Connection Type | Plain | Enumeration
Specifications | Safety Valve Connection Type | Threaded | Enumeration
Specifications | Condensate Drain Type | Plain | Enumeration
Specifications | Flue or Air Intake Classification | B23 | Text | Flue/air intake classification standard, e.g. 'B23'
Application Data
Specifications | Reference Standard | BS, EN | Text | BS, EN, ISO
Dimensional Data
Specifications | Overall Length | 1926 | mm | Depth or Diameter
Specifications | Overall Width | 1281 | mm
Specifications | Overall Height | 1826 | mm
Specifications | Gross Weight | 3066 | kg | Equates to operating weight
Specifications | Water Content | 561 | litres
Specifications | Shipping Weight | 2505 | kg | Equates to dry weight of unit plus packaging allowance
Specifications | Access Clearance Top | 0 | mm | Access required for maintenance of this item
Specifications | Access Clearance Bottom | 0 | mm | Access required for maintenance of this item
Specifications | Access Clearance Left | 400 (depending on door handing) | mm | Access required for maintenance of this item
Specifications | Access Clearance Right | Burner length + 100 | mm | Access required for maintenance of this item
Specifications | Access Clearance Front | 2300 (1400 with shorter cleaning rods) | mm | Access required for maintenance of this item
Specifications | Access Clearance Rear | 820 | mm | Access required for maintenance of this item
Specifications | Fuel Connection Size | R 2" |  | Choose units from dropdown
Specifications | Flow and Return Connection Size | DN150 |  | Choose units from dropdown
Specifications | Drain Connection Size | R3/4" |  | Choose units from dropdown
Specifications | Safety Valve Connection Size | DN65 (when using optional safety manifold) |  | Choose units from dropdown
Specifications | Condensate Drain Size | N/A |  | Choose units from dropdown
Specifications | Flue Connection Size | 360 | mm | Also state whether internal or external in notes
Specifications | Air Inlet Connection Size | N/A | mm | Also state whether internal or external in notes
Performance Data
Specifications | Sound Pressure Level | 75 (dependent on burner) | dBA | Measured at 1m from the casing
Specifications | Primary Fuel | Gas - NG | Enumeration
Specifications | Optional Fuel | Oil - 35/sec | Enumeration | If Not Applicable, choose 'No Optional Fuel'
Specifications | Gas Consumption rate | 64 | m3/h | If Not Applicable Mark '0'
Specifications | Oil Consumption rate | 52 | kg/h | If Not Applicable Mark '0'
Specifications | Rated Output | 511 - 570 | kW | Product rated output
Specifications | Rated Criteria | 80/60 | Enumeration | Flow and Return differential
Specifications | ErP Rated Efficiency at Full Load | 0 | % | Gross Rated Efficiency at 100% Load, above 70kW. If Not Applicable Mark '0'
Specifications | ErP Rated Efficiency at Part Load | 0 | % | Gross Rated Efficiency at 30% Load, above 70kW. If Not Applicable Mark '0'
Specifications | ErP Seasonal Efficiency | 0 | % | Seasonal Efficiency, below 70kW. If Not Applicable Mark '0'
Specifications | Building Regulations Seasonal Efficiency | 86.3 | % | Refer to Building Regulations
Specifications | Turndown Ratio | Dependent on burner used | Text | Ratio of maximum to minimum fire
Specifications | NOx Emissions | 128 - gas 160 - Oil | mg/kWh | NOx Emissions at 0% O2
Specifications | Hydraulic Resistance at 11C temperature differential | 83 | mbar | Hydraulic Resistance at 11ºC Δt
Specifications | Hydraulic Resistance at 20C temperature differential | 25 | mbar | Hydraulic Resistance at 20ºC Δt
Specifications | Minimum Flow Rate at 11C temperature differential | 0 | l/s | Minimum flow rate at 11ºC Δt
Specifications | Minimum Flow Rate at 20C temperature differential | 0 | l/s | Minimum flow rate at 20ºC Δt
Specifications | Maximum Operating Pressure | 6 | bar | Water side
Specifications | Minimum Operating Pressure | 0.8 | bar | Water side
Specifications | Nominal Gas Inlet Pressure | 20 | mbar | Standard gas inlet pressure. If Not Applicable Mark '0'
Specifications | Minimum Gas Inlet Pressure | 16.9 (dependent on gas train used) | mbar | Minimum safe gas inlet pressure. If Not Applicable Mark '0'
Specifications | Maximum Gas Inlet Pressure | 25 | mbar | Maximum safe gas inlet pressure. If Not Applicable Mark '0' | en-UK | en-UK
Specifications | Nominal Oil Inlet Pressure | 50 | mbar | Standard oil inlet pressure. If Not Applicable Mark '0'
Specifications | Minimum Oil Inlet Pressure | -0.40 (for twin pipe circuits) | mbar | Minimum safe oil inlet pressure. If Not Applicable Mark '0'
Specifications | Maximum Oil Inlet Pressure | 400 | mbar | Maximum safe oil inlet pressure. If Not Applicable Mark '0'
Specifications | Water Treatment Required | Y | Y/N | State whether product requires water treatment. If yes, refer to manufacturer's instructions.
Electrical Data
Specifications | Voltage | 230 | Volts
Specifications | Supply Phase | 1 | Number | 1,3
Specifications | Frequency | 50 | Hertz | eg. N/A, DC, 50,60, Other, UserDefined
Specifications | IP Rating | Dependent on burner used | Text | Ingress Protection rating e.g. IP56
Specifications | IK Rating | NA | Text | Impact Resistance rating
Specifications | Starting Current | 4.8 (dependent on burner used) | Amps
Specifications | Full Load Current | 2.8 (dependent on burner used) | Amps
Specifications | Fuse Rating | 10 | Amps | At UK standard voltage
Specifications | Maximum Power Consumption | Dependent on burner used | W
Specifications | Minimum Power Consumption | Dependent on burner used | W
Controls
Specifications | Control Type | Weather compensating, Optimiesd SS, on,off | Text | e.g. Weather compensating, Optimised Start/Stop, On/Off
Specifications | BMS Links | Y | Y/N
Specifications | Interlocks | Y | Y/N
Sustainability
Sustainable Material BREEAM etc | Embodied Carbon |  | kgCO2e | Awaiting industry standard
Sustainable Material BREEAM etc | Life Cycle Analysis |  | Number | Awaiting industry standard
Sustainable Material BREEAM etc | Location of Manufacturer |  | GridRef | Awaiting industry standard
Sustainable Material BREEAM etc | Green Guide for Specification |  | Enumeration | A - E (Awaiting industry standard)
Sustainable Material BREEAM etc | Environmental Product Declaration |  | Text | 3rd Party Verification (Awaiting industry standard)
Sustainable Material BREEAM etc | Responsible Sourcing of Materials |  | Enumeration | Endorsing body (Awaiting industry standard)
Sustainable Material ETL | Energy Technology List | 0 | URL | Hyperlink to ETL webpage for product. If Not Applicable Mark '0'
Sustainable Material LEED v.4 | Responsible Extraction of Materials |  | Text | Awaiting industry standard
Sustainable Material LEED v.4 | Material Ingredient Reporting |  | Text | Awaiting industry standard
Sustainable Product Directive Ecodesign | ErP Energy Label | 0 | Text | State ErP efficiency class. If Not Applicable Mark '0'
Operations & Maintenance
Facilities/Asset Management | O&M Manual | http://www.bosch-industrial.co.uk/GE615 | URL | Hyperlink to Manufacturer O&M Data
Facilities/Asset Management | Daily | 0 | Text | Maintenance tasks or SFG20 codes. If Not Applicable Mark '0'
Facilities/Asset Management | Weekly | Water pressure check | Text | Maintenance tasks or SFG20 codes. If Not Applicable Mark '0'
Facilities/Asset Management | Monthly | 0 | Text | Maintenance tasks or SFG20 codes. If Not Applicable Mark '0'
Facilities/Asset Management | Quarterly | 0 | Text | Maintenance tasks or SFG20 codes. If Not Applicable Mark '0'
Facilities/Asset Management | 6 Monthly | Annual maintenance (oil firing) | Text | Maintenance tasks or SFG20 codes. If Not Applicable Mark '0'
Facilities/Asset Management | Annually | Annual maintenance (gas) | Text | Maintenance tasks or SFG20 codes. If Not Applicable Mark '0'
Facilities/Asset Management | Bespoke Timeframe | 0 | Text | Maintenance tasks or SFG20 codes. If Not Applicable Mark '0'
Facilities/Asset Management | Maintenance Required 0-300hrs | 0 | Text | Maintenance tasks required during this time frame. If Not Applicable Mark '0'
Facilities/Asset Management | Maintenance Required 301-600hrs | 0 | Text | Maintenance tasks required during this time frame. If Not Applicable Mark '0'
Facilities/Asset Management | Maintenance Required 601-1000hrs | 0 | Text | Maintenance tasks required during this time frame. If Not Applicable Mark '0'
Facilities/Asset Management | Maintenance Required 1001-2000hrs | 0 | Text | Maintenance tasks required during this time frame. If Not Applicable Mark '0'
Facilities/Asset Management | Maintenance Required 2001-4000hrs | 0 | Text | Maintenance tasks required during this time frame. If Not Applicable Mark '0'
Facilities/Asset Management | Maintenance Required 4001-8000hrs | 0 | Text | Maintenance tasks required during this time frame. If Not Applicable Mark '0'
Facilities/Asset Management | Maintenance Required 8001-12000hrs | 0 | Text | Maintenance tasks required during this time frame. If Not Applicable Mark '0'
Facilities/Asset Management | Expected Life | 15 - 20 | Years
Facilities/Asset Management | Warranty ID | Customer registration | Text
This spreadsheet is the property of CIBSE although it can be freely used in the ways described, and completed with data specific to particular products. It is important that the Categories and Parameters given on the form are not changed. It is also important that where units of measurement are defined on the form that these too are followed. Any comment or suggestion on their revision should be addressed to pdt@cibse.org